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1. Purpose and Effect
This Addendum revises and supplements Attachment A (Overhead Bid Unit Definitions), Attachment B (Underground Bid Unit Definitions), Attachment C (Pricing Workbook), and the emergency make-safe billing instructions in the 2026 Street Light Operations & Maintenance Request for Proposals (RFP).
Except as expressly modified by this Addendum, the RFP remains unchanged. If this Addendum conflicts with an earlier provision of the RFP, this Addendum governs. Respondents shall use the final revised Attachment C issued with this Addendum when preparing their proposals.
The revisions below clarify existing work boundaries and add discrete operational units needed for diagnosis, safety, restoration, and temporary hazard protection. Units shall not be stacked for the same labor, equipment, travel, or productive work unless a unit expressly states that it may accompany another authorized unit.
2. Emergency Make-Safe Authorization and Billing
PLA's one-hour emergency response requirement remains unchanged. For emergency make-safe work, a dispatch recorded in the Asset Management System or documented by email or text from PLA's authorized designee constitutes written T&E approval solely to eliminate or secure the immediate hazard.
The Contractor shall bill actual labor at the applicable Straight Time, Overtime, or Double Time rate and actual equipment at the rates in Attachment C. The Contractor shall not also bill a unit price, OH18, UG43, a separate trip charge, or duplicate labor or equipment for the same time and scope.
Permanent repair after the immediate hazard is secured requires a written work order identifying the applicable unit price or continued written T&E authorization. Emergency dispatch authority does not authorize unrelated or permanent work beyond the make-safe scope.
3. Attachment A — Overhead Unit Amendments
Attachment A is amended by replacing the listed Work included language for the clarified units and adding the new units below. All general inclusions and exclusions in Attachment A continue to apply.
3.1 Clarified Existing Units
OH6  Overhead wire fault repair — secondary
	Change
	Clarified definition

	Unit
	EA

	Work included
	Isolate and locate one secondary overhead-conductor fault within one span; make permanent repair, including up to 10 ft of conductor and up to 6 joints or connectors; test and restore service. Record voltage, cause of failure, repair details, and at least 3 geo-tagged photographs when damage is involved. Replacement of an entire span is paid under OH8.



OH18  Overhead OK on arrival / unsuccessful field visit
	Change
	Clarified definition

	Unit
	EA

	Work included
	Travel to and inspect one overhead work-order location where the asset is operating on arrival, access is unavailable, the location is incorrect, or the site is not ready. Document the condition and photographs. No other unit or T&E travel charge is payable for the same visit.



OH20  Guy-wire assembly
	Change
	Clarified definition

	Unit
	EA

	Work included
	Install or replace one overhead guy or down-guy assembly, including attachment hardware, tensioning, and testing. Where the guy supports a span luminaire, remove and reattach the luminaire as required.



3.2 New Overhead Units
OH22  Diagnostic testing at luminaire location
	Change
	New unit

	Unit
	EA

	Work included
	Test the luminaire, document voltage and photocell or shorting-cap operation, and repair one termination if needed. Not payable with a fixture, photocell, driver, module, or wiring replacement unit at the same location.



OH23  Diagnostic testing at lighting control / feed — street accessible
	Change
	New unit

	Unit
	EA

	Work included
	Test a street-accessible lighting control or feed point, document voltage and control operation, and repair one termination if needed. Not payable with a lighting-controller replacement unit at the same location.



OH24  Diagnostic testing at lighting control / feed — easement or backlot
	Change
	New unit

	Unit
	EA

	Work included
	Access an easement or backlot feed point, climb as required, test and document voltage and control operation, and repair one termination if needed. Not payable with a lighting-controller replacement unit at the same location.



OH25  Replace in-line fuse holder and fuse
	Change
	New unit

	Unit
	EA

	Work included
	Replace one in-line fuse holder and fuse at a luminaire or pole-mounted feed point; test and restore service.



OH26  Re-sag overhead conductor / span
	Change
	New unit

	Unit
	SPAN

	Work included
	Re-sag one existing overhead conductor span and complete required terminations. Conductor or full-span replacement is excluded and is paid under the applicable span unit.



4. Attachment B — Underground Unit Amendments
Attachment B is amended by replacing the listed Work included language for the clarified units and adding the new units below. All general inclusions and exclusions in Attachment B continue to apply.
4.1 Clarified Existing Units
UG9  Repair conduit / duct at one location
	Change
	Clarified definition

	Unit
	EA

	Work included
	Locate, expose, and repair one conduit or duct failure at one location; includes excavation, backfill, compaction, and soft-surface restoration. Extensive conduit replacement is paid under UG7 or UG8. Hard-surface cutting and restoration are paid under UG47, UG48, UG50, or UG51 as applicable.



UG43  Underground OK on arrival / unsuccessful field visit
	Change
	Clarified definition

	Unit
	EA

	Work included
	Travel to and inspect one underground work-order location where the asset is operating on arrival, access is unavailable, the location is incorrect, or the site is not ready. Document the condition and photographs. No other unit or T&E travel charge is payable for the same visit.



UG47  Saw cutting concrete or asphalt
	Change
	Clarified title and definition

	Unit
	LF

	Work included
	Saw cut concrete or asphalt to the limits required for authorized streetlight work, measured by linear foot. Removal and restoration are paid under the applicable restoration unit.



UG48  Remove and replace concrete
	Change
	Clarified definition

	Unit
	SF

	Work included
	Remove, lawfully dispose of, and replace concrete to match the existing thickness, line, grade, finish, and adjoining surface, measured by square foot. Curb replacement is paid under UG51.



4.2 New Underground Safety and Restoration Units
UG50  Remove and replace asphalt pavement
	Change
	New unit

	Unit
	SF

	Work included
	Remove damaged asphalt, lawfully dispose of material, prepare and compact the base, and place asphalt to match the adjoining thickness, line, grade, and surface, measured by square foot.



UG51  Remove and replace concrete curb
	Change
	New unit

	Unit
	LF

	Work included
	Remove and lawfully dispose of existing curb; form and replace concrete curb to match the adjoining line, grade, section, and finish, measured by linear foot.



UG52  Manhole confined-space safety setup
	Change
	New unit

	Unit
	PER DAY

	Work included
	Provide and remove the confined-space entry setup for one crew for one day, including atmospheric testing, ventilation, retrieval equipment, attendant, barriers, and required documentation. This unit may accompany another authorized manhole-work unit because it prices required entry protection, not productive repair work.



UG53  Handhole / vault cleaning
	Change
	New unit

	Unit
	EA

	Work included
	Clean one handhole, vault, or manhole by removing silt, debris, and foreign material; lawfully dispose of removed material and document condition before and after. Dewatering, when separately required, is paid under UG15.



UG54  Cable termination with splices
	Change
	New unit

	Unit
	EA

	Work included
	Complete up to three terminations or splices of 600V insulated cable, #2/0 AWG or smaller, at one location; test, label, document, and restore service.



UG55  Temporary hot box / exposed-cable protection
	Change
	New unit

	Unit
	EA

	Work included
	Install and secure a temporary protective enclosure over underground conductors exposed by a pole knockdown or other hazard; label the enclosure, document installation, and remove it when the permanent repair is completed.



5. Attachment C — Partition II Tree-Trimming Amendment
The Partition II introductory note is revised to state: Priced only by Respondents bidding Partition II. No trimming unit includes tree or stump removal. No minimum volume is guaranteed.
TT-5  Backlot distribution-pole access trimming
	Change
	New Partition II unit

	Unit
	EA

	Work included
	Create safe climbing and working clearance at one DTE backlot distribution-pole location serving PLA street lighting, including a 5 ft radius around the pole and access path as directed; remove debris and leave the site clean.



6. Revised Attachment C Pricing Workbook
Respondents shall use the final revised Attachment C issued with this Addendum and shall not add, delete, combine, rename, or otherwise alter pricing lines. Each unit price includes the labor, supervision, equipment, mobilization, routine traffic control, soft restoration, waste handling, and documentation stated in the applicable unit-definition attachment unless a unit expressly states otherwise.
PLA shall complete the estimated annual quantity and evaluation treatment for every new unit before issuance. The evaluated subtotal shall use the quantities and formulas in the final revised workbook. Contingent units remain excluded from the evaluated subtotal unless the final issued workbook states otherwise.
The labor, equipment, and markup tabs apply only when PLA has authorized T&E or other reimbursable work under the RFP and Contract. A unit-priced task shall not also be billed on T&E for the same time and scope.
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